Spanish (Espanol)

Esta informe contiene informacion muy importante sobre la calidad de su agua potable.  Por favor lea este informe o comuniquese con alguien que pueda tradiucir la informacion.

We're pleased to present to you this year's Annual Quality Water Report. This report is designed to inform you about the quality water and services we deliver to you every day. Our constant goal is to provide you with a safe and dependable supply of drinking water. We want you to understand the efforts we make to continually improve the water treatment process and protect our water resources. We are committed to ensuring the quality of your water. Our water wells draw from the Lower Rio Grande Aquifer.

If you have any questions about this report or concerning your water utility, please contact Ernesto Carranza at 575-589-1075.  We want our valued customers to be informed about their water utility.

Camino Real Regional Utility Authority routinely monitors for contaminants in your drinking water according to Federal and State laws. This table shows the results of our monitoring for the period of January 1 to December 31, 2018. As water travels drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency's (EPA) Safe Drinking Water Hotline (800-426-4791). The sources of drinking water (both tap water and bottled water) include rivers, lakes, streams, ponds, reservoirs, springs, and wells. As water travels over the surface of the land or through the ground, it dissolves naturally occurring minerals and, in some cases, radioactive material, and can pick up substances resulting from the presence of animals or from human activity: microbial contaminants, such as viruses and bacteria, that may come from sewage treatment plants, septic systems, agricultural livestock operations, and wildlife; inorganic contaminants, such as salts and metals, which can be naturally occurring or result from urban stormwater runoff, industrial, or domestic wastewater discharges, oil and gas production, mining, or farming; pesticides and herbicides, which may come from a variety of sources such as agriculture, urban stormwater runoff, and residential uses; organic Chemical Contaminants, including synthetic and volatile organic chemicals, which are by-products of industrial processes and petroleum production, and can also come from gas stations, urban stormwater runoff, and septic systems; and radioactive contaminants, which can be naturally occurring or be the result of oil and gas production and mining activities. In order to ensure that tap water is safe to drink, EPA prescribes regulations that limit the amount of certain contaminants in water provided by public water systems. Food and Drug Administration (FDA) regulations establish limits for contaminants in bottled water which must provide the same protection for public health.

All sources of drinking water are subject to potential contamination by substances that are naturally occurring, or manmade. These substances can be microbes, inorganic or organic chemicals and radioactive substances. All drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency’s Safe Drinking Water Hotline at 1-800-426-4791.

How can I get Involved? Public meetings are held once a month. Please contact the water utilities office at (575)-589-1075 for more information of date and time.

Regulated Contaminants

The table below presents a summary of results of water testing done by the NMED Drinking Water Bureau and by the Utility Authority during the 2016 calendar year. Detected contaminants from 2013 through 2014 are also listed, if not sampled in 2016. The table contains the name of each contaminant, the highest level allowed by regulation (MCL), the ideal goals for public health (MCLG), the highest single amount found among all samples taken, the expected sources of such contamination, and the incidence of violations.

Maximum Contaminant Level (MCL): The highest level of a contaminant that is allowed in drinking water. MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

Maximum Contaminant Level Goal (MCLG): The level of a contaminant in drinking water below, for which there is no known or expected risk to health, i.e. zero risk. The MCL usually accepts a risk of 1 in 1,000,000 or 1 in 100,000 persons.

Action Level (AL): The concentration of a contaminant which, if exceeded, triggers treatment or other requirements that the water supply system must follow.

| TEST RESULTS |
| --- |
| Contaminant (Unit Measurement) | Violation Y/N | Range of Levels Detected | Highest Level Detected | Date Tested | MCLG | MCL | Likely Source of Contamination |
| Microbiological Contaminants: |
| Total Coliform Bacteria | NO | Absent |  | 2018 | Absent | presence of coliform bacteria in 5% of monthly samples | Naturally present in the environment |
| Radioactive Contaminants: |
| Beta/photon emitters (pCi/1) | NO | 4.4- 10.5 | 10.5 | 2016 | 0 | 4 | Decay of natural and man-made deposits |
| Combined radium 226/228 (pCi/1) | NO | 0.35 – 0.35 | 0.35 | 2017 | 0 | 5 | Erosion of natural deposits |
| Organic Contaminants: |
| Di (2 - ethylhexyl) Phthalate | NO | Not Detected | 1 | 2016 | 0 | 6 | Discharge from rubber and chemical factories |
| Disinfection By-Products: |
| Chlorine (ppm) | NO | 0 - .485 | .485 | 2018 | 4 | 4 | Water additive used to control microbes |
| Total Trihalomethanes (ppb) | NO | 1.2 - 28 | 27 | 2018 | < 40 | 80 | Disinfection byproduct |
| 25. Total Haloacetic Acid (ppb) | NO | 0 – 4.9 | 4 | 2018 | No goal for the total | 60 | Disinfection byproduct |
| ADDITIONAL TEST RESULTS Contaminant (Unit Measurement) Violation Y/N Range of Levels Detected Highest Level Detected Date Tested MCLG MCL Likely Source of Contamination |
| Inorganic Contaminants: |
| Arsenic (ppb) | YES | 13 – 18 | 18 | 2018 | 0 | 10 | Erosion of natural deposits; runoff from orchards; runoff from glass and electronics production wastes |
| Barium (ppm) | NO | .026 - .058 | .058 | 2017 | 2 | 2 | Discharge of drilling wastes; discharge from metal refineries; erosion of natural deposits |
| Fluoride (ppm) | NO | .70 – 1.2 | 1.2 | 2017 | 4 | 4 | Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories |
| Nitrate (as Nitrogen) (ppm) | NO | 0 – .061 | 1 | 2018 | 10 | 10 | Runoff from fertilizer use; leaching from septic tanks, sewage; erosion of natural deposits |
| Selenium (ppb) | NO | 3.5- 6.3 | 6.3 | 2017 | 50 | 50 | Discharge from petroleum and metal refineries; erosion of natural deposits; discharge from mines |
| Volatile Organic Contaminants: |
| Xylenes (ppm) | NO | 0.0008 | 0.0008 | 2018 | No goal for the total |  |  |
| Lead and Copper: |
| Lead and Copper | Violation Y/N | Action Level (AL) | 90th Percentile | Date Sampled | MCLG | # Sites Over AL | Likely Source of Contamination |
| Copper- action level at consumer taps. (ppm) | NO | 1.3 | .26 | 2017 | 1.3 | 0 | Corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |
| Lead - action level at consumer taps. (ppb) | NO | 15 | 3.1 | 2017 | 0 | 1 | Corrosion of household plumbing system; Erosion of natural deposit |

If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children.  Lead in drinking water is primarily from materials and components associated with service lines and home plumbing.  Camino Real Regional Utility Authority is responsible for providing high quality drinking water but cannot control the variety of materials used in plumbing components.  When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking.  If you are concerned about lead in your water, you may wish to have your water testing.  Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline or at http://www.epa.gov/safewater/lead

| Arsenic: |
| --- |
| Some people who drink water containing arsenic in excess of the MCL over many years could experience skin damage or problems with their circulatory system and may have an increased risk of getting cancer. |
| Violation Type | Violation Begins | Violation Ends | Violation Explanation |
| MCL, Average | 1/01/2014 | 03/31/2014 | Water samples showed that the amount of this contamination in our drinking water was above its standard (called a maximum contaminant level and abbreviated MCL) for the period indicated. |
| MCL, Average | 4/01/2014 | 06/30/2014 | Water samples showed that the amount of this contamination in our drinking water was above its standard (called a maximum contaminant level and abbreviated MCL) for the period indicated. |
| MCL, Average | 1/01/2018 | 03/31/2018 | Water samples showed that the amount of this contamination in our drinking water was above its standard (called a maximum contaminant level and abbreviated MCL) for the period indicated. |
| MCL, Average | 04/01/2018 | 6/30/2018 | Water samples showed that the amount of this contamination in our drinking water was above its standard (called a maximum contaminant level and abbreviated MCL) for the period indicated. |
| MCL, Average | 07/01/2018 | 9/30/2018 | Water samples showed that the amount of this contamination in our drinking water was above its standard (called a maximum contaminant level and abbreviated MCL) for the period indicated. |
| MCL, Average | 10/01/2018 | 12/31/2018 | Water samples showed that the amount of this contamination in our drinking water was above its standard (called a maximum contaminant level and abbreviated MCL) for the period indicated. |
| SOLUTIONS TO ARSENIC VIOLATIONS: CRRUA is currently working with contracted Engineers to design an Arsenic Treatment Plant for the Border that would address the only issue remaining for the CRRUA Water Utility. |

Monitoring and Report Violations

Camino Real Regional Utility Authority was required to submit a Sampling Plan to the state for the various drinking water standards.  We failed to submit this Sampling Plan to the New Mexico Environment Department Drinking Water Bureau (NMED DWB) for approval within the required timeframes and it resulted in a violation.

What should you do?

There is nothing that needs to be done at this time.

What does this mean?

The quality of the water is not compromised; however, failure to complete and submit this Sampling Plan is a requirement of the drinking water regulations.

What happened?  What is being done?

The Camino Real Regional Utility Authority water system completed and submitted a Sampling Plan to the NMED-Drinking Water Bureau, and we are now back in compliance.

Source Water Assessment and Assessment and Protection Program (SWAPP)

The Camino Real Regional Utility Authority is well maintained and operated, and sources of drinking water are generally protected from potential sources of contamination based on well construction, hydro geologic settings, and system operations and management. The susceptibility rank of the entire water system is moderately HIGH please contact the Camino Real Regional Utility Authority to discuss the findings of the SWAPP report.

Thank you for allowing us to continue providing your family with clean, quality water this year. In order to maintain a safe and dependable water supply we sometimes need to make improvements that will benefit all of our customers. These improvements are sometimes reflected as rate structure adjustments. Thank you for understanding.

Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by cryptosporidium and other microbiological contaminants are available from the Safe Drinking Water Hotline (800-426-4791).

We at Camino Real Regional Utility Authority work around the clock to provide top quality water to every tap. We ask that all our customers help us conserve and protect our water sources, which are the heart of our community, our way of life and our children’s future.

Contacts for Information:

Brent Westmoreland, Executive Director, Camino Real Regional Utility Authority

Phone: (575) 589 - 1075

PO Box 429, Sunland Park, NM 88063 • www.crrua.org

NMED Drinking Water Bureau

Phone: (575) 524-6300

1170 N. Solano, Las Cruces 88005 • www.nmenv.state.nm.us

EPA Safe Drinking Water Hotline: 800-426-4791

www.epa.gov/safewater/dwhealth.html • www.epa.gov/ogwdw/agua/apsalud.html (in Spanish)

EPA Office of Ground Water and Drinking Water

www.epa.gov/ogwdw • www.epa.gov/safewater/agua.html (in Spanish)

American Water Works Association: www.awwa.org

The Groundwater Foundation: www.groundwater.org

# Text boxes

Water Report

2018 Consumer Confidence Report

Key to units:

ppm = parts per million, or milligrams per liter (mg/L)

ppb = parts per billion, or micrograms per liter (μg/L)

pCi/L = picocuries per liter (a measure of radioactivity)

mrems/yr = millirems per year (a measure of radioactive exposure over time)